## A
Battery Power Consumption for Radio Transmitter/Reciever
Version 2.1
Item | Description | Symbol | Result | Units
Current Drain
1 | Instrument Element/Meter Current Drain | Aie | 100 | mA
2 | Transmitter Current Drain | Ate | 280 | mA
3 | Receiver Current Drain | Are | 0 | mA
4 | Modem Current Drain | Ame | 0 | mA
Stand-by Current Drain
5 | Instrument Element/Meter Current Drain | Aid | 10 | mA
6 | Transmitter Current Drain | Atd | 15 | mA
7 | Receiver Current Drain | Ard | 15 | mA
8 | Modem Current Drain | Amd |  | mA
Equipment Cycle Time Information
Name | Turbidity Meter
| Instrument Element/Meter Data Cycle Time | tic | 1 | min
| Instrument Element/Meter ON-time | tie | 0.5 | min or | 30 | sec
| Instrument Element/Meter OFF-time | tid | 0.5 | min
Name | Transceiver
| Transceiver/Modem Cycle Time | ttc | 1440 | min
| ON-time | tte | 30 | min or | 1800 | sec
| OFF-time | ttd | 1410 | min
Rechargeable Battery Specifications
9 | Battery Voltage | BV | 12 | V
10 | Battery Rating | BR | 10000 | mAhr
11 | Quantity of Batteries | Q | 1
Battery Life Calculations
12 | Safety Factor to Apply to Calcs | SF | 50 | %
13 | Battery Life (hours) | BLh | 110.8545 | hours / | 1.5 | = | 73.903 | hours
14 | Battery Life (days) | BLd | 4.6189 | days / | 1.5 | = | 3.0793 | days
| Current and Power Drain |  | 0.090208 | A | and |  | 1.0825 | W
Notes:
1 | Modem current drain included in transmitter and receiver current drain numbers.
2 | Data for turbidity meter is assumed and should be confirmed.
3 | On-times, off-times, and cycle times should be confirmed.
4 | Voltage requirements for instruments should be confirmed.
5 | Trickle battery charger (solar or other) should be sized to exceed battery current drain x2.
6 | Ambient conditions (ie. extreme temperatures) may shorten battery life.
7 | Input values into green shaded cells and worksheet is protected to prevent accidental changes but is not password protected.
8 | This worksheet is free to copy and use.
© 1998 - 2017, John Hibberd & HEI Group. All rights reserved.