## A
Table 1: | Sizing Operations
Unit Operation: | Chlorination and Dechlorination Dosing Requirements - Version 2.1
|  |  | SODIUM HYPOCHLORITE |  | SODIUM METABISULPHITE
Item | Description | Symbol | Result | Units | Result | Units
1 | Input Target Tot. Residual Chlorine Concentration | TRC | 25 | mg/L | 50 | mg/L
2 | Input Tot. Residual Chlorine Demand | DTRC | 0 | mg/L
3 | TRC Dosing Concentration Required | RTRC | 25 | mg/L
4 | Input Process Water Flow | Q | 100 | IGPM | 100 | IGPM
|  |  | 119.549 | usgpm | 119.549 | usgpm
|  |  | 452.837 | L/m | 452.837 | L/m
5 | Input Supplied Concentration of Chemical | C | 12 | trade% (mg/100 mL) | 35 | wt% (mg/100 mg)
6 | Input Specific Gravity of Chemical | SG | 1.04 |  | 1.35
Results
7 | Dose Rate of Chemical | D | 94.341 | mL/min | 64.2118 | mL/min
|  |  | 135.8511 | L/day | 92.465 | L/day
|  |  | 35.8647 | USGPD | 24.4108 | USGPD
Calculation for Water Recirculation Systems (i.e. Cooling Towers)
| Chemical Dose IN | D | 94.341 | mL/min
| Flow Fraction of Total Dose |  | 100 | % of Tot. Dose
| Water Flow IN | Qin | 452.837 | L/m
| Flow Fraction of Total Flow |  | 100 | % of Tot. Water Flow
| Water Flow OUT | Qout | 452.83 | L/m
| Flow Fraction of Total Flow |  | 99.9984 | % of Tot. Water Flow
| Recirculation Water Flow | Qr | 0.10137 | L/m
| Flow Fraction of Total Flow |  | 0.022384 | % of Tot. Water Flow
Resultant Dosing TRC Concentration
| Input Target Tot. Residual Chlorine Concentration | TRC | 25 | mg/L
| Input Tot. Residual Chlorine Demand | DTRC | 0 | mg/L
| TRC Dosing Concentration Required | RTRC | 25 | mg/L
| Resultant Stream TRC Concentrations |  |  |  | Check Total
| Concentration of Water OUT | Cout | 25 | mg/L | 25.0056 | mg/L
| Resultant Recirc Concentration | Cr | 25 | mg/L
| Additional TRC from Recirc (as a result of dilution) | Cr+ | 0.0055961 | mg/L
© 1998 - 2017, John Hibberd & HEI Group. All rights reserved.
Notes:
1. Input values into yellow and green shaded cells.
2. Worksheet is protected to prevent accidental changes but is not password protected.
3. This worksheet is free to copy and use.