## A
On-Site Generation of Chlorine - Sizing Program
Version 1.1 - March 31, 1999
Input Process Parameters
| Cooling Water Flow Rate | 600 | usgpm
| Target Residual Chlorine Concentration | 0.5 | mg/L as Cl2
| Chlorine Demand | 0.5 | mg/L as Cl2
| Total Residual Chlorine Dose | 1 | mg/L as Cl2
| Seawater Salinity | 35000 | ppm as NaCl or
|  | 3.5 | % salt
| Molecular Weight of NaCl | 58.44 | g/g-mole
| Molecular Weight of Cl | 35.45 | g/g-mole
** | Chloride Concentration in Seawater | 21231.1773 | ppm as Cl
| Ratio of Salt Required per lb Cl2 Produced | 19 | lb salt/lb Cl2
| Density of Seawater | 62.43 | lb/ft3
Calculated Requirements
| Minimum Chlorine Dose | 0.005 | lb/min as Cl2
|  | 7.2 | lb/day as Cl2
| Minimum Salt Requirement | 136.8 | lb of salt as NaCl/day
| Minimum Chloride Concentration | 3908.5714 | lb of Water/day
| Minimum Volume of Seawater | 468.2243 | usgpd
|  | 0.32516 | usgpm
|  | 1.2317 | L/min
Electrical Requirements
| Power Supply | 8 | VDC
| Power Required per 1 lb of Cl2 | 2.88 | KWH
| Current Required per 1 lb of Cl2 | 15 | amperes
| System Power Required | 20.736 | KWH
| System Current Required | 108 | amperes
Find Number of Cells for Generator
| Input per cell | 120 | VAC
|  | 1 | amperes
|  | 2.88 | KWH
| Output per cell | 6.5 | VDC
|  | 20 | amperes
|  | 3.12 | KWH
| Number of cells required | 7.2 | cells
| Recommended to Use | 8 | cells
Cost Estimate
| Cost per lb of Cl2 (or Cost per Cell) | 1500 | $/lb Cl2 (or $/cell)
| Total Cost for On-Site Chlorine Generator | 12000 | $/Generator
** | Value for Chloride Concentration over estimates actual seawater concentration due to assumption that seawater salt is in form of NaCl. Should be approx. 19000 ppm for seawater
References:
1 | Safe-T-Clor Website at http://home.att.net/~Safe-T-clor.
2 | White, G.C., Handbook of Chlorination and Alternative Disinfectants, Third Edition, (Van Nostrand Reinhold, New York, 1992) p.168 - 183.
© 1999 - 2017, John Hibberd & HEI Group. All rights reserved.