## A
Flow Dilution Test - Version 1.1
Item | Description | Result 1 | Units 1 | Results 2 | Units 2 | Results 3 | Units 3
1 | Pipe Dia | 42 | inches or | 3.5 | feet
2 | Pipe Length | 8000 | feet
3 | Flow Min | 20000 | m3/day or | 706000 | ft3/day | 3666.6667 | usgpm
4 | Flow max | 80000 | m3/day or | 2824000 | ft3/day | 14666.6667 | usgpm
5 | Pipe X-Section Area | 9.6163 | ft2
6 | Flow Velocity Min | 73417.3924 | ft/day or | 50.9843 | ft/min
7 | Flow Velocity Max | 293669.5697 | ft/day or | 203.9372 | ft/min
8 | Max Residence Time | 156.911 | min or | 2.6152 | hours
9 | Min Residence Time | 39.2278 | min or | 0.6538 | hours
Stock Solution Make-up |  |  |  |  | Summary
Item | Description | Result 1 | Units 1 |  | Safety Factor to Apply to Volumes |  |  | 1.2 | times
1 | Water Flow (Max) | 80000 | m3/day |  | Mass of LiCl Required |  |  | 4887.3901 | g of LiCl
2 | Dosing Period | 60 | minutes |  | Approx. volume of LiCl solution |  |  | 97.7478 | L of Soln
3 | Minumum Target Li Concn | 0.2 | mg/L
4 | Molecular Weight of Li | 6.939 | g/mole |  | Dosing Rate of LiCl Soln |  |  | 1.3576 | L/min
5 | Molecular Weight of LiCl | 42.392 | g/mole
6 | Target LiCl Concn | 1.2218 | mg/L
7 | Multiplier | 0.00084851
8 | Mass of LiCl Required | 4072.8251 | g
9 | Solubility of LiCl in water | 637 | g/L at 0 oC
10 | Percent LiCl in raw crystals | 100 | %
11 | Specific Gravity of LiCl crystals | 2.07
12 | Target LiCl Concn in Stock Soln | 50 | g/L
13 | Total Volume of effluent water plus LiCl crystals | 81.4565 | L of LiCl soln
14 | Approx. Volume of effluent water to add to LiCl crystals | 79.489 | L of water
15 | Stock Solution Concentration | 50000 | mg/L as LiCl
16 | Stock Solution Concentration | 8184.3272 | mg/L as Li
17 | Stock Solution Dosing Rate | 1.3576 | L/min or | 1357.6084 | mL/min
Stock Solution Dilution Standards
| Minimum Dilution (Vol Basis) | 10230.409 | to 1
| Maximum Dilution (Vol Basis) | 40921.6362 | to 1
Item | Dilution Steps (in mL) | Dilution Ratio | Select Standards
1 | 10:1000 + 25:500 | 1:2000
2 | 10:1000 + 20:500 | 1:2500
3 | 25:2000 + 25:1000 | 1:3200
4 | 10:1000 + 25:1000 | 1:4000
5 | 10:1000 + 20:1000 | 1:5000
6 | 25:2000 + 25:2000 | 1:6400 | x
7 | 10:1000 + 25:2000 | 1:8000 | x
8 | 10:1000 + 20:2000 | 1:10000 | x | x
9 | 25:2000 + 25:2000 + 500:1000 | 1:12800 | x
10 | 50:500 + 25:2000 + 25:500 | 1:16000 | x
11 | 50:500 + 10:1000 + 25:500 | 1:20000 | x | x
12 | 50:500 + 10:1000 + 20:500 | 1:25000 | x
13 | 50:500 + 25:2000 + 25:1000 | 1:32000 | x
14 | 50:500 + 10:1000 + 25:1000 | 1:40000 | x | x
15 | 50:500 + 10:1000 + 20:1000 | 1:50000 | x
16 | 50:500 + 25:2000 + 25:2000 | 1:64000 | x | x
17 | 50:500 + 10:1000 + 25:2000 | 1:80000
18 | 50:500 + 10:1000 + 20:2000 | 1:100000
| Example: | Make a 1:2000 solution:
| Step #1 | Add 10 mL of stock solution to 1000 mL of effluent (i.e. 10:1000)
| Step #2 | Now add 25 mL of the step #1 solution to 500 mL of effluent (i.e. 25:500)
Summary nomenclature is therefore 10:1000 + 25:500.
© 1998 - 2017, John Hibberd & HEI Group. All rights reserved.

## B
TABLE 1.0: FLOW DATA FOR |  |  | COMPANY ABC INC.
Date (dd-mm-yy): |  | 1999-06-25
LiCl Dose (mL/min): |  | 1250
LiCl Mass Used (g as LiCl): |  | 5000
Volume of LiCl Solution (L) |  | 95
LiCl Stock Concn (mg/L as Li): |  | 8616.7294
Time | Instrument | LiCl Concentration | LiCl Concentration | LiCl Concentration | LiCl Flow | Flow Difference | Flow Difference
(hh:mm) | Flow (L/min) | measured (mg/l) | background (mg/l) | demand (mg/l) | (L/min) | (L/min) | (%)
11:30 | 27800 | 0.4 | 0 | 0 | 26927.2793 | 872.7207 | 3.241
11:45 | 27800 | 0.45 | 0 | 0 | 23935.3594 | 3864.6406 | 16.1462
12:00 | 27800 | 0.44 | 0 | 0 | 24479.3448 | 3320.6552 | 13.5651
12:15 | 27800 | 0.4 | 0 | 0 | 26927.2793 | 872.7207 | 3.241
12:30 | 27800 | 0.39 | 0 | 0 | 27617.7223 | 182.2777 | 0.66
12:45 | 27800 | 0.42 | 0 | 0 | 25645.0279 | 2154.9721 | 8.4031
13:00 | 27800 | 0.4 | 0 | 0 | 26927.2793 | 872.7207 | 3.241
13:15 | 27800 | 0.41 | 0 | 0 | 26270.5164 | 1529.4836 | 5.8221
13:30 | 27800 | 0.41 | 0 | 0 | 26270.5164 | 1529.4836 | 5.8221
13:45 | 27800 | 0.45 | 0 | 0 | 23935.3594 | 3864.6406 | 16.1462
14:00 | 27800 | 0.42 | 0 | 0 | 25645.0279 | 2154.9721 | 8.4031
14:15 | 27800 | 0.44 | 0 | 0 | 24479.3448 | 3320.6552 | 13.5651
|  |  |  | Average | 25755.0047 | 2044.9953 | 8.188
|  |  |  | Min | 23935.3594 | 182.2777 | 0.66
|  |  |  | Max | 27617.7223 | 3864.6406 | 16.1462
|  |  |  | Std Dev | 1225.5927 | 1225.5927 | 5.2111
|  |  |  | Maximum data error |  | 16.1462
|  |  |  | Tolerance of LiCl test |  | 4.062
|  |  |  | TOTAL ERROR |  | 20.2082
Flow Calibration Curve Data
Date (dd-mm-yy): |  | 1994-11-26
LiCl Dose (mL/min): |  | 1250
LiCl Stock Concn (mg/L as Li): |  | 8616.7294
Sample Dilution | LiCl Concentration | LiCl Concentration | Equivalent Flow | Equivalent Flow | Slope | y-intercept | Slope | y-intercept | Avg Calc | Flow Difference
Ratio | measured (mg/l) | expected (mg/L) | (L/min) | (m^3/day) | measured | measured | expected | expected | Flow (L/min) | Error (%)
10000 | 0.84 | 0.86167 | 12500 | 18000 |  |  |  |  | 12808.658 | 2.4693
20000 | 0.43 | 0.43084 | 25000 | 36000 | -1.0351 | 9.253 | -1 | 9.2846 | 24923.2029 | -0.30719
40000 | 0.21 | 0.21542 | 50000 | 72000 | -0.96717 | 9.3104 | -1 | 9.2846 | 50818.54 | 1.6371
64000 | 0.13 | 0.13464 | 80000 | 115200 | -0.98005 | 9.2903 | -1 | 9.2846 | 81860.2384 | 2.3253
|  |  |  | Average | -0.99412 | 9.2845 | -1 | 9.2846
|  |  |  | Min | -1.0351 | 9.253 | -1 | 9.2846
|  |  |  | Max | -0.96717 | 9.3104 | -1 | 9.2846
Standard Deviation of Concentration of Stock Solution (A) is: |  |  | 1/2 x measuring error + 1/2 x reading error
1.25
Standard deviation of feed rate of stock solution (B) is: |  |  | 1/2 x equipment error
1
Standard deviation of concentration of effluent sample (C) is: |  |  | 1/2 x reading error + 1/2 x concentrate error
1.25
Total standard deviation (TSD) is: |  |  | SQRT(A^2+B^2+C^2)
2.031
Tolerance is : | 2 x TSD | % | 4.062
Dosing Pump Error for: |  | COMPANY ABC INC.
Dose Before | Dose After | Average Dose | % Error
ml/min | ml/min | ml/min
9.49 | 10.6 | 10.045 | 11.0503
NOTES:
Inout new values into shaded cells.