## A
Heat Balances Calculator
| Version: | 1.1
| Date: | June 1999
The following calculations determine how much heat is required to heat up a known volume of air.
| Determine heat requirements for heating n moles of air for a dT = |  |  |  |  | 20 | oC?
| Tin | 10 | oC |  | Building Dimensions
| Tout | -10 | oC |  | L | 16 | ft
| Pressure | 1 | atmos |  | W | 12 | ft
| Coeff | 393.72 |  |  | H | 10 | ft
| for | 0.04147 |  |  | vol chg/hr | 2
| Cv | 2.1273e-05 |  |  | Bldg vol | 1920 | ft3
|  | -9.825e-09 |  |  | Air Vol | 3840 | ft3/hr | 64 | cfm
| Cv | 393.7615 | J/mol |  | Moles/L | 0.044643
| n | 80.9389 | moles/min |  | moles/ft3 | 1.2647
| Hj | 31870.6185 | J/min |  | total moles/hr | 4856.3335
| Hbtu | 30.208 | Btu/min |  | tot moles/min | 80.9389
| Hj x 2 | 63741.237 | J/min | (with 2 x safety factor) |  | Add | 1062.3539 | W to case results
| Hbtu x 2 | 60.4159 | Btu/min | (with 2 x safety factor) |  | Add | 60.4159 | Btum to case results
CASE 1
LOOK AT NORMAL STEEL ENCLOSURE with 2 in thick insulation
| kair= | 0.02227 | W/m.K | Refer to page 736 in HX text
| Pr= | 0.722 |  | Reference temp for properties of air is:
| v= | 9.49e-06 | m2/s
| uf= | 1.488e-05 | kg/m.s
| p= | 1.4128 | kg/m3
| Cp= | 1.0053 | KJ/kg.oC
| Twin= | 283 | K
| Tf= | 263 | K
| Area F1 | 17.8465 | m2 (L x W) | Area F2 | 14.8721 | m2 (L x H) | Area F3 | 11.1541 | m2 (W x H)
| vel= | 20 | m/s
| Material | Heat Transfer Coefficient, k |  | Material Thickness
| Steel | 43 | W/m.oC | 0.125 | in | 0.0031758 | m
| Foam | 0.027 | W/m.oC | 2 | in | 0.050813 | m
Face | Avg T | Re | hmo |  | Qface | Qtot | Twin | Two | Tfi | Tfo | Tf
Name | K |  | W/m2.oC |  | W/face | W (2 faces) | oC | oC | oC | oC | oC
Ref.
F1 | 273 | 8903085.7003 | 58.3302 |  | 187.9391 | 375.8783 | 10 | 9.9992 | 9.9992 | -9.8195 | -10
|  |  |  | check | 187.9391
F2 |  | 8127368.1158 | 59.2865 |  | 156.6387 | 313.2775 | 10 | 9.9992 | 9.9992 | -9.8223 | -10
|  |  |  | check | 156.6387
F3 |  | 7038507.2542 | 60.8082 |  | 117.5052 | 235.0104 | 10 | 9.9992 | 9.9992 | -9.8268 | -10
|  |  |  | check | 117.5052
|  |  | Surface Loss |  |  | Surface Loss + Air Heating
Case 1 Results: |  |  | 924.1661 | W |  | 1986.5201 | W
|  |  | 52.5572 | Btum |  | 112.9732 | Btum
Notes:
| 1. | 1062.3539 | W was added to case results
listed above to heat air in 1 minute
|  | to achieve a dT = | 20 | oC
| 2. | The above results are approximately proportional to the surface
area of the box enclosure.
Therefore, if a 2 cu. ft box is used instead of a 1 cu. ft box then as a rough estimate
just double the heat requirement results for each case.
| 3. | The above calculations are based on a carbon steel box,
with and w/o a layer of insulation on all 6 faces of box.
© 1998 - 2017, John Hibberd & HEI Group. All rights reserved.