## A
V-Notch Flow Calculation Sheet - Version 1.1
General Formula: |  | Q = Cd x (8/15) x (2 x g)^(1/2) x Tan (a/2) x h^(5/2)
|  | where : | Q = Flow (cfs)
Cd = discharge coefficient
g = gravity acceleration (32.174 f/(s^2))
a = notch angle
h = head on weir
Input angle of weir |  | a = | 53.5 | degrees
Form of Equation |  | Q = | 2.1564 | Cd x h^(5/2)
Raw Data from Weir Design Data Graphs | [6 empty] | Interpolation for a
h | Ce for 90 | Ce for 45 | Ce for 22.5 | Ratio 90:45 | Ratio 90: 22.5 | Ratio 45:22.5 | 53.5 | degree v-notch weir
0.2 | 0.6028 | 0.6111 | 0.641 | 0.98642 | 0.94041 | 0.95335 |  | 0.62346
0.3 | 0.5934 | 0.6037 | 0.625 | 0.98294 | 0.94944 | 0.96592 |  | 0.61049
0.4 | 0.5882 | 0.5987 | 0.6158 | 0.98246 | 0.95518 | 0.97223 |  | 0.60312
0.5 | 0.586 | 0.5952 | 0.6098 | 0.98454 | 0.96097 | 0.97606 |  | 0.59887
0.6 | 0.585 | 0.5928 | 0.6054 | 0.98684 | 0.9663 | 0.97919 |  | 0.59603
0.7 | 0.5847 | 0.5911 | 0.6028 | 0.98917 | 0.96997 | 0.98059 |  | 0.59449
0.8 | 0.5846 | 0.59 | 0.6005 | 0.99085 | 0.97352 | 0.98251 |  | 0.5932
0.9 | 0.5846 | 0.5891 | 0.599 | 0.99236 | 0.97596 | 0.98347 |  | 0.59239
1 | 0.5848 | 0.5883 | 0.5978 | 0.99405 | 0.97825 | 0.98411 |  | 0.59183
1.1 | 0.585 | 0.5879 | 0.5966 | 0.99507 | 0.98056 | 0.98542 |  | 0.59127
1.2 | 0.5853 | 0.5874 | 0.5954 | 0.99642 | 0.98304 | 0.98656 |  | 0.59076
FLOW TABLE FOR V-NOTCH WEIRS
New Modified Equation for | [6 empty] | Max | 0.62346
| Q= | 1.2911 | h^(2.5) |  |  |  | Min | 0.59076
| where a= | 53.5 | degrees |  |  |  | Avg | 0.59872
[7 empty] | Std | 0.0096851
h (ft) | Q (cfs) | Q (usgpm) | Q (cu. m/hr)
0 | 0 | 0 | 0
0.2 | 0.023096 | 10.366 | 2.3544
0.3 | 0.063644 | 28.5654 | 6.488
0.4 | 0.13065 | 58.6391 | 13.3185
0.5 | 0.22823 | 102.4382 | 23.2664
0.6 | 0.36003 | 161.5902 | 36.7014
0.7 | 0.5293 | 237.5648 | 53.9573
0.8 | 0.73906 | 331.7126 | 75.3407
0.9 | 0.99211 | 445.2903 | 101.1372
1 | 1.2911 | 579.478 | 131.6148
1.1 | 1.6385 | 735.3916 | 167.0269
1.2 | 2.0366 | 914.0924 | 207.6146
© 1998 - 2017, John Hibberd & HEI Group. All rights reserved.